Application No.:  347790

Equipment Category - Boiler

| 1. GENERAL INFORMATION |  |  | DATE: 12/2/1999 |
| --- | --- | --- | --- |
| a. manufacturer: Nebraska |  |  |  |
| b. type: Boiler |  | c. model: Boiler No. 1: NS-C-48-Econ Boiler No. 2: NS-B-42-Econ Boiler No. 3: NS-B-42-Econ |  |
| d. style: Watertube type |  |  |  |
| e. applicable aqmd regulation xi rules: 1146 |  |  |  |
| f. cost: $ ( ) source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 347790 |
| --- | --- | --- | --- |
| A. FUNCTION: Hot Water and Steam |  |  |  |
| B. maximum Heat Input: Boiler No. 1: 33.9 MMBtu/hr Boiler No. 2: 24.2 MMBtu/hr Boiler No. 3: 24.2 MMBtu/hr |  | C. maximum throughput: Burner: Coen, Model 750, Delta NOx-20 Burner: Coen, Model 730, Delta NOx-16 Burner: Coen, Model 730, Delta NOx-16 |  |
| D. burner information: no.: 1 type: See above |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: Amber 363 |  |
| g. operating conditions: Load following, with short periods of steady-state operation. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 347790 |
| --- | --- | --- | --- |
| A. NAME: Children's Hospital Los Angeles |  |  |  |
| B. ADDRESS: 4850 Sunset Blvd. CITY: Los Angeles STATE: CA ZIP: 90027 |  |  |  |
| C. CONTACT PERSON: Mr. Robert Hollowell |  | D. PHONE NO.: (323) 483-5333 |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 347790 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Sean Cullins |  |  | D. PHONE NO.: (909) 396-2655 |  |
| E. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 347790-347792 ISSUANCE DATE: 12/2/1999 check if no p/c |  |  |  |  |
| F. START-UP DATE: 1-20-00 |  |  |  |  |
| G. PERMIT TO OPERATE INFORMATION: P/O NO.: ISSUANCE DATE: |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 347790 |
| --- | --- | --- | --- |
| A. PERMIT |  |  |  |
| A1. PERMIT LIMIT: 7 ppm NOx @ 3% O2, 50 ppm CO @ 3% O2, 5 ppm NH3 @ 3% O2 |  |  |  |
| A2. bact/lAer DETERMINATION: See above permit limits. |  |  |  |
| B. CONTROL TECHNOLOGY |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Peerless |  |  |  |
| B2. TYPE: Selective Catalytic Reduction |  |  |  |
| B3. DESCRIPTION: The factory designed add-on air pollution control equipment consists of a honeycomb type catalyst bed with an anhydrous ammonia injection grid. The system (i.e., the programmable logic controller) will be programmed with computational fluid dynamics modeling and actual field data during startup, and this information will be combined into an algorithm that determines the right quantity of ammonia to inject into the catalyst bed. Also, the catalyst bed has a "sponge effect" feature that minimizes the NOx and ammonia spikes created during rapid load change periods. |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 354741-2, 356262 ISSUANCE DATE: 12/2/1999 P/O NO.: ISSUANCE DATE: |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: HP |  |  |  |
| B6. WARRANTY: 2-year guarantee that the system will achieve compliance with the required emissions limits. The expected catalyst life is 5-7 years. |  |  |  |
| B7. PRIMARY POLLUTANTS: VOC, NOX, SOX, CO, PM10 |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |
| B9. SPACE REQUIREMENT: UNKNOWN |  |  |  |
| B10. LIMITATIONS: The temperature window for optimum operation is 425-700 degrees Fahrenheit. |  |  |  |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: TOSCO Refining Company CONTACT PERSON: Miles Heller PHONE NO.: (310) 952-6120 AGENCY: SCAQMD ADDRESS: Diamond Bar, CA CONTACT PERSON: Ngoc Tran PHONE NO.: (909) 396-2606 |  |  |  |
| B12. OPERATING HISTORY: None |  |  |  |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: PERFORMANCE DATA: |  |  |  |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: |  |  |  |
| C. COST |  |  |  |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $175,000 (each) INSTALLATION: $ (1999) SOURCE OF COST DATA: |  |  |  |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $6,000-7,000/year (1999) SOURCE OF COST DATA: |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |
| D5. FREQUENCY OF MAINTENANCE: |  |  |  |

| 6. COMMENTS |  | App. No.: 347790 |
| --- | --- | --- |
| The equipment will be source tested by an independent contractor shortly after start-up to verify compliance with the NOx, CO, and ammonia emissions limits specified in the permit. While operating with natural gas, the equipment will be tested at minimum, average, and maximum loads. While operating with Amber 363, the equipment will be tested at maximum load. In addition to the initial source tests, a NOx analyzer will be installed to monitor and record the NOx emissions from the SCR unit. An AQMD certified CEMS was not required for this project. Staff has also received a request to further explain the transfer of technology from the previous demonstration example noted in Section 5, Item B11. This information will be added to this BACT listing in the near future. |  |  |