Application No.:  413617

Equipment Category - Boiler

| 1. GENERAL INFORMATION |  |  | DATE: 7/11/2003 |
| --- | --- | --- | --- |
| a. manufacturer: Johnston |  |  |  |
| b. type: Firetube |  | c. model: PFTA250-4-155 |  |
| d. style: |  |  |  |
| e. applicable aqmd rules: 1146 |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 413617 |
| --- | --- | --- | --- |
| A. FUNCTION: Hot water |  |  |  |
| B. maximum Heat Input: 10 MMBtu/hr |  | C. maximum throughput: |  |
| D. burner information: no.: 1 type: Ultra Low-NOx |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: None |  |
| g. operating conditions: Two identical boilers. Seasonal use--in heating season, one is generally in use while the second is kept on at minimum fire. In summer months, one boiler is shut down and the other is kept on at minimum fire. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 413617 |  |
| --- | --- | --- | --- | --- |
| A. NAME: Fullerton College |  |  |  | B. SIC CODE: |
| C. ADDRESS: 321 E. Chapman Ave. CITY: Fullerton STATE: CA ZIP: 92832 |  |  |  |  |
| D. CONTACT PERSON: Arrion Cotton |  | E. PHONE NO.: 714-448-3327 |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 413617 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Ray Ronquillo |  |  | D. PHONE NO.: 909-396-3049 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 413617 ISSUANCE DATE: 4/24/2003 check if no p/c P/O NO.: ISSUANCE DATE: |  |  |  |  |
| F. START-UP DATE: March 2003 |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 413617 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: Maximum emissions (ppmvd@3%O2): NOx-12, CO-50. Compliance with Rule 1146. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: Emission limits (ppmvd@3%O2): NOx-12, CO-50 |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: AQMD BACT guidelines (Part D, non-major polluting sources). |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Johnston Burner Co. (subsidiary of Johnston Boiler Co.) |  |  |  |  |  |
| B2. TYPE: Forced internal recirculation (FIR) |  |  |  |  |  |
| B3. DESCRIPTION: This burner has a central ceramic cylinder protruding into the flame zone. Air is injected via a ring of orifices outboard of the central cylinder. Windbox pressure is relatively high, at typically 26 " H2O, creating high velocity air jets. Gas is injected into the center of each air orifice via spuds extending from a ring plenum. Flue gas is drawn from the end of the cylinder into the base of the flame via slots in the cylinder near the furnace wall. The high velocity jets induce the flue gas recirculation. |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: Johnston guarantees 12 ppm NOx and 50 ppm CO, both ppmvd@3%O2 |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM10, SOx |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: None |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: The boiler started up in March 2003. After some initial adjustments, the burner has been running fine and has not required further attention. |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: None DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: Manufacturer recommends inspect refractory and check/adjust O2 every six months. |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: 4/18/2003 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: Boiler 1 Boiler 2 Low Mid High Low Mid High O2, % (dry) 4.4 4.6 4.7 5.6 5.3 5.1 NOx, ppmvd@3%O2 6.0 8.3 7.8 <5.9* <5.8* 6.5 CO, ppmvd@3%O2 <22* <22* <22* <23* <23* <23* OPERATING CONDITIONS: TEST METHODS: AQMD Method 100.1. *Some results were less than 20% of the instrument range and therefore were reported as less than that figure. |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 413617 |
| --- | --- | --- |
| Johnston Burner Co. licenses the FIR technology, for use in firetube boilers, from the Gas Research Institute (GTI). GTI developed the technology in cooperation with the Southern California Gas Co. |  |  |