- Application No.:  358625

Equipment Category – Gas Turbine, Landfill or Digester Gas Fired

| 1. GENERAL INFORMATION |  |  | DATE: 9/24/2003 |
| --- | --- | --- | --- |
| a. manufacturer: Solar |  |  |  |
| b. type: Combined Cycle |  | c. model: MARS-90-13000 |  |
| d. style: |  |  |  |
| e. applicable aqmd rules: 1134 |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 358625 |
| --- | --- | --- | --- |
| A. FUNCTION: One of three identical gas turbines, each driving an electrical generator. Each gas turbine exhausts through an unfired heat recovery steam generator (HRSG). Steam generated from three HRSGs drives a 5.1 MW steam turbine generator. This permit is for modification of the turbine to update its firing system, which also entailed an increase in power rating. |  |  |  |
| B. maximum Heat Input: 113 MMBtu/hr |  | C. maximum throughput: 9.9 MW |  |
| D. burner information: no.: type: Annular |  |  |  |
| e. primary fuel: Digester Gas |  | f. other fuel: Natural Gas |  |
| g. operating conditions: Steady, Full-Load |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 358625 |  |
| --- | --- | --- | --- | --- |
| A. NAME: Los Angeles County Sanitation Districts |  |  |  | B. SIC CODE: 4952 |
| C. ADDRESS: 24501 S. Figueroa Street CITY: Carson STATE: CA ZIP: 90745 |  |  |  |  |
| D. CONTACT PERSON: Preeti Ghuman |  | E. PHONE NO.: 562-699-7411 x2138 |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 358625 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Hassan Namaki |  |  | D. PHONE NO.: 909-396-2699 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 358625 ISSUANCE DATE: 7/25/2000 check if no p/c P/O NO.: ISSUANCE DATE: |  |  |  |  |
| F. START-UP DATE: 3/31/2002 (Estimated at time of Application) |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 358625 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: Fuel to gas turbine to be minimum 60 vol.% digester gas (24-hr avg.). Heat input to gas turbine not to exceed 113 MMBtu/hr. Compliance with Rule 1134 (limits NOx to 25 ppmvd@15%O2 multiplied by electrical efficiency [HHV]/25). CO not to exceed 60 ppmvd@15%O2. CEMS for NOx and O2. Annual performance test for NOx and CO. Mass emissions limits (lb/hr): NOx-12, CO-16.3, ROG-4.5 (as C), PM-5.7, SOx-1.3. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: NOx and CO limits of 25 and 60 ppmvd@15%O2, respectively |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: NOx: AQMD BACT Guidelines, Part D; CO: based on source test result. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Solar |  |  |  |  |  |
| B2. TYPE: Water Injection |  |  |  |  |  |
| B3. DESCRIPTION: Atomized water is injected into the combustion zone of the turbine to lower flame temperature and thus reduce NOx formation. |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 358625 ISSUANCE DATE: 7/25/2000 P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, ROG, PM |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: None |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: 7/1-3/2002 and 10/7/2002 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: Load 6MW 9MW NOx, PPMVD@15%O2 22.6 22.7 CO, PPMVD@15%O2 55.5 31.1 NMHC, PPMVD NM 3.21 PM, lb/hr NM 4.64 (NM = Not Measured) OPERATING CONDITIONS: TEST METHODS: AQMD Methods: 1.1-4.1 for volumetric flow rate, 5.1 for PM, 25.3 for NMHC, 100.1 for NOx and CO. |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 358625 |
| --- | --- | --- |