Application No.:  361525

Equipment Category – I.C. Engine-Stationary, Non-Emergency

| 1. GENERAL INFORMATION |  |  | DATE: 1/17/2002 |
| --- | --- | --- | --- |
| a. manufacturer: Ford |  |  |  |
| b. type: spark ignition |  | c. model: LSG875 |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: 1110.2 |  |  |  |
| f. cost: $30,000 (1999) source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 361525 |
| --- | --- | --- | --- |
| A. FUNCTION: Engine drives an electrical generator |  |  |  |
| B. maximum Heat Input: |  | C. maximum throughput: 93 BHP |  |
| D. burner information: no.: type: |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: lpg stand by fuel |  |
| g. operating conditions: Used as back-up, but allowed to operate more than 200 hrs/yr |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 361525 |
| --- | --- | --- | --- |
| A. NAME: Crestline Village Water District |  |  |  |
| B. ADDRESS: 777 Cottonwood Drive CITY: Crestline STATE: CA ZIP: 92325 |  |  |  |
| C. CONTACT PERSON: Norm Hunt |  | D. PHONE NO.: 909-338-1727 |  |

| 4. PERMIT INFORMATION |  |  | App. No.: 361525 |
| --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  |  |  |
| B. AGENCY CONTACT PERSON: Roy Olivares |  | C. PHONE NO.: 909-393-2208 |  |
| D. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 361525 ISSUANCE DATE: 11/16/1999 |  |  |  |
| E. START-UP DATE: 11/99 |  |  |  |
| F. PERMIT TO OPERATE INFORMATION: P/O NO.: F34242 ISSUANCE DATE: 10/06/2000 |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 361525 |
| --- | --- | --- | --- |
| A. PERMIT |  |  |  |
| A1. PERMIT LIMIT: Emission limits (gr/bhp-hr): NOx: 0.15, VOC: 0.15, CO: 0.6 |  |  |  |
| A2. bact/lAer DETERMINATION: (gr/bhp-hr) VOC: 0.15, NOx: 0.15, CO: 0.6 |  |  |  |
| B. CONTROL TECHNOLOGY |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Miratech, Model MN-09-04F-D2, with Miratech Model MEC-2001-air/fuel ratio controller |  |  |  |
| B2. TYPE: 3-way catalytic converter and air/fuel ratio controller |  |  |  |
| B3. DESCRIPTION: The NOx, VOC, and CO emissions in the exhaust gas are converted to N2, CO2/H2O, and CO2, respectively, in the presence of a catalyst. The air/fuel ratio controller ensures that the O2 concentration in the exhaust gas stays at or below 0.5% (the optimum exhaust gas mixture favored by the catalyst). |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: none ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: HP |  |  |  |
| B6. WARRANTY: |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, VOC, CO |  |  |  |
| B8. SECONDARY POLLUTANTS: none |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |
| B10. LIMITATIONS: |  |  |  |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: CONTACT PERSON: PHONE NO.: AGENCY: ADDRESS: CONTACT PERSON: PHONE NO.: |  |  |  |
| B12. OPERATING HISTORY: |  |  |  |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 7/25/01 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: PERFORMANCE DATA: |  |  |  |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: Engine operating at 84 BHP, generator output 60 kW, fuel input 14.4 scfm, O2<.05%. Emissions in g/bhp-hr: VOC .02, NOx <0.103, CO 0.34. |  |  |  |
| C. COST |  |  |  |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $8,000 INSTALLATION: $ (1999) SOURCE OF COST DATA: |  |  |  |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ () SOURCE OF COST DATA: |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: Source test 7/25/01 |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |
| D5. FREQUENCY OF MAINTENANCE: |  |  |  |

| 6. COMMENTS |  | App. No.: 361525 |
| --- | --- | --- |
| The NOx result in the source test was actually 0.0 ppmvd (O2<.05%). However, the NOx analyzer was on 100 ppm range, and therefore the NOx was only proven to be <20 ppmvd. |  |  |