Application No.:  362406

Equipment Category – I.C. Engine - Stationary, Non-Emergency

| 1. GENERAL INFORMATION |  |  | DATE: 12/22/1999 |
| --- | --- | --- | --- |
| a. manufacturer: Tecodrive |  |  |  |
| b. type: spark ignited |  | c. model: 7400LE |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: 1110.2 |  |  |  |
| f. cost: $ ( ) source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 362406 |
| --- | --- | --- | --- |
| A. FUNCTION: Four engines will be used to drive two compressors/chillers that will provide cooling for the facility. |  |  |  |
| B. maximum Heat Input: |  | C. maximum throughput: 171 brake horsepower |  |
| D. burner information: no.: type: |  |  |  |
| e. primary fuel: natural gas |  | f. other fuel: none |  |
| G. operating conditions: steady-state/full load Operating schedule: 6 hours/day average, 24 hours/day max |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 362406 |
| --- | --- | --- | --- |
| A. NAME: Kaiser Permanente Health Plan, Inc. |  |  |  |
| B. ADDRESS: 6041 Cadillac Drive CITY: Los Angeles STATE: CA ZIP: 90034 |  |  |  |
| C. CONTACT PERSON: Mr. Norair Edgarian |  | D. PHONE NO.: (323) 783-8442 |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 362406 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Roy Olivares |  |  | D. PHONE NO.: (909) 396-2208 |  |
| E. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 362406 ISSUANCE DATE: 12/14/1999 check if no p/c |  |  |  |  |
| F. START-UP DATE: |  |  |  |  |
| G. PERMIT TO OPERATE INFORMATION: P/O NO.: ISSUANCE DATE: |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 362406 |
| --- | --- | --- | --- |
| A. PERMIT |  |  |  |
| A1. PERMIT LIMIT: NOx =< 0.15, VOC =< 0.15, CO =< 0.60 (units are grams/BHP-hr) |  |  |  |
| A2. bact/lAer DETERMINATION: same as above |  |  |  |
| B. CONTROL TECHNOLOGY |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Miratech and Tecodrive |  |  |  |
| B2. TYPE: Miratech, Model MN-11T-04F, catalytic converter Tecodrive, air/fuel ratio controller |  |  |  |
| B3. DESCRIPTION: The NOx, VOC, and CO emissions in the exhaust gas are converted to N2, CO2/H2O, and CO2, respectively, in the presence of a catalyst. The air/fuel ratio controller ensures that the O2 concentration in the exhaust gas stays within the range required for optimum catalyst performance. |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |
| B6. WARRANTY: |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, VOC, and CO |  |  |  |
| B8. SECONDARY POLLUTANTS: none |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |
| B10. LIMITATIONS: |  |  |  |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: 1998 SCAQMD BACT guidelines FACILITY: CONTACT PERSON: PHONE NO.: AGENCY: ADDRESS: CONTACT PERSON: PHONE NO.: |  |  |  |
| B12. OPERATING HISTORY: |  |  |  |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: PERFORMANCE DATA: |  |  |  |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: |  |  |  |
| C. COST |  |  |  |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $16,792 (for 2 engines) INSTALLATION: $ (1999) SOURCE OF COST DATA: |  |  |  |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ () SOURCE OF COST DATA: |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |
| D5. FREQUENCY OF MAINTENANCE: |  |  |  |

| 6. COMMENTS |  | App. No.: 362406 |
| --- | --- | --- |
| The engine will be source tested to verify compliance with the NOx, CO, and VOC emission limits specified in the permit. Along with this application, the applicant submitted three additional applications (A/Ns 362407-9) for identical engines at the same location. There will be two engines per chiller, and the cost of each chiller is $188,986. |  |  |