Application No.:  245157

Equipment Category – Landfill Gas Gathering System

| 1. GENERAL INFORMATION |  |  | DATE: 06/08/2001 |
| --- | --- | --- | --- |
| a. manufacturer: |  |  |  |
| b. type: Landfill Gas Flaring System (4 new flares being added to existing 3-flare system) |  | c. model: |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: 1150.1 |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 245157 |
| --- | --- | --- | --- |
| A. FUNCTION: Burns landfill gas to destroy organic gases. |  |  |  |
| B. maximum Heat Input: 248 MMBtu/hr |  | C. maximum throughput: 8750 scfm |  |
| D. burner information: no.: one per flare type: hexagonal, spud-type |  |  |  |
| e. primary fuel: landfill gas |  | f. other fuel: |  |
| g. operating conditions: Landfill gas flow and Btu value vary with weather conditions and gradually decline over time. One or more flares may be shutdown when gas flow is low. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 245157 |  |
| --- | --- | --- | --- | --- |
| A. NAME: City of Los Angeles, Bureau of Sanitation |  |  |  | B. SIC CODE: 4953 |
| C. ADDRESS: 11950 Lopez Canyon Road CITY: Los Angeles STATE: CA ZIP: 91342 |  |  |  |  |
| D. CONTACT PERSON: John Hamilton |  | E. PHONE NO.: 818-834-5115 |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 245157 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Linda Dejbakhsh |  |  | D. PHONE NO.: 909-396-2614 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: ISSUANCE DATE: 8/28/1991 check if no p/c P/O NO.: F38381 ISSUANCE DATE: 3/29/ 2001 |  |  |  |  |
| F. START-UP DATE: 12/91 (estimate at time of application) |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 245157 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: Maximum landfill gas flow rate: 8750 scfm total, 1250 scfm per flare. Minimum temperature in flare stack: 1400 deg F. Maximum emission rates, lb/hr per flare (total all flares): NOx 2.1 (9.4), SOx 0.38 (2.7), CO 0.35 (2.5), PM 0.63 (4.8), NMHC 0.63 (4.4). Maximum pollutant concentrations: NOx .06 lb/MMBtu, CO .01 lb/MMBtu, PM 6.1 lb/MMSCF landfill gas. Minimum NMHC destruction efficiency of 98% or maximum NMHC concentration in stack of 20 ppm, dry corrected to 3% O2 as hexane (as required by Rule 1150.1). |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: Maximum NOx concentration: .06 lb/MMBtu. Minimum temperature in flare stack: 1400 deg F. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: BACT Guidelines, Part D. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: |  |  |  |  |  |
| B2. TYPE: |  |  |  |  |  |
| B3. DESCRIPTION: |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: Carmelta Benitez DATE: 2/2/01 |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: Facility found to be in compliance with permit conditions |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: Numerous DATES: 1991 - 11/28/00 CAUSES: None relating to the flare station (reviewed back to 1997). |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: 8/99 (3 flares tested), 8/00 (one flare tested) CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: 98.3 (8/99, avg.), 98.5 (8/00) OVERALL EFFICEINCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: For these tests, the flares were operating at approx. 40-60% of their max. permitted flow rate. The following pollutant concentrations were found: NOx .045 lb/MMBtu or less, CO .008 lb/MMBtu or less, PM 4.79 lb/MMSCF landfill gas or less. TEST METHODS: |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 245157 |
| --- | --- | --- |
| In this example, the landfill gas flares are being operated with pollutant concentrations below the following limits: NOx .06 lb/MMBtu, CO .01 lb/MMBtu, PM 6.1 lb/MMSCF landfill gas. This NOx limit is already contained in Part D of the BACT Guidelines (guidelines for non-major facilities). The CO and PM limits are thus the significant information in this listing. The CO limit of .01 lb/MMBtu appears to be a relatively low limit and may not be achievable in all cases. |  |  |