Section : BACT Determination for Application No.:	335644

Equipment Category - Spray Booth

| 1. GENERAL INFORMATION |  |  | DATE: 5/25/1999 |
| --- | --- | --- | --- |
| a. manufacturer: Devilbiss |  |  |  |
| b. type: Dry Filter |  | c. model: 2000 |  |
| d. style: Automotive downdraft type |  |  |  |
| e. applicable aqmd regulation xi rules: 1151 & 1171 |  |  |  |
| f. cost: $Not applicable ( ) source of cost data: |  |  |  |
| g. operating schedule: 8 hrs/day 5 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 335644 |
| --- | --- | --- | --- |
| A. size/dimension/capacity: 14'-4" W. x 24'-4" L. x 11'-2" H. |  |  |  |
| B. blowers: 1 @ 5 HP |  | C. total flow rate: 10000 scfm |  |
| D. filters: 5 @ 24" x 72" |  |  |  |
| e. Parts coated: Motor vehicles - auto body |  |  |  |
| f. type of coating/adhesive/solvent used: Primer, top coat |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 335644 |
| --- | --- | --- | --- |
| A. NAME: Bob Wondries Ford |  |  |  |
| B. ADDRESS: 1301 W. Valley Blvd. CITY: Alhambra STATE: CA ZIP: 91801 |  |  |  |
| C. CONTACT PERSON: Peter James |  | D. PHONE NO.: (818) 282-5496 |  |

| 4. PERMIT INFORMATION |  |  | App. No.: 335644 |
| --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  |  |  |
| B. AGENCY CONTACT PERSON: Jeanne Pandes Villacorte/AQ Engineer |  | C. PHONE NO.: (909) 396-2621 |  |
| D. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 335644 ISSUANCE DATE: |  |  |  |
| E. START-UP DATE: 12/97 |  |  |  |
| F. PERMIT TO OPERATE INFORMATION: P/O NO.: F11713 ISSUANCE DATE: 2/4/1998 |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 335644 |
| --- | --- | --- | --- |
| A. PERMIT |  |  |  |
| A1. PERMIT LIMIT: 30 lbs/day (900 lbs/month) VOC |  |  |  |
| A2. bact/lAer DETERMINATION: The BACT/LAER determination for this application is a haptite adsorber (concentrator) coupled with a catalytic oxidizer. Permit requires an overall efficiency of 83%. The basis for this efficiency was not based upon source test results but the minimum efficiency required to increase throughput without increasing emissions and thus avoiding offsets. |  |  |  |
| B. CONTROL TECHNOLOGY |  |  |  |
| B1. MANUFACTURER/SUPPLIER: ITW Devilbiss - Envirocure |  |  |  |
| B2. TYPE: Concentrator |  |  |  |
| B3. DESCRIPTION: A haptite concentrator with two beds vents a downdraft automotive type, totally enclosed spray booth/oven where both compliant coatings are used. The bed is desorbed with hot air and vented through a catalytic oxidizer @ 650 degrees F. The oxidizer has a 600,000 Btu/hr natural gas fired burner and a 5 HP exhaust fan. |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 335644 ISSUANCE DATE: P/O NO.: F11713 ISSUANCE DATE: 2/4/1998 |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: 10,000 ACTUAL CONTAMINANT LOADING: BLOWER HP: 15 HP |  |  |  |
| B6. WARRANTY: Non known |  |  |  |
| B7. PRIMARY POLLUTANTS: VOC |  |  |  |
| B8. SECONDARY POLLUTANTS: NOx, CO |  |  |  |
| B9. SPACE REQUIREMENT: Non known |  |  |  |
| B10. LIMITATIONS: |  |  |  |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: Non known CONTACT PERSON: PHONE NO.: AGENCY: SCAQMD ADDRESS: CONTACT PERSON: PHONE NO.: |  |  |  |
| B12. OPERATING HISTORY: Operating since 12/97 |  |  |  |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 4/8/98 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: 89.80% PERFORMANCE DATA: |  |  |  |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: Flow rate during spraying: 589 dscfm Recirc. flow rate during spraying: 7940 scfm Flowrate during curing: 488 dscfm Flow rate during cooling: 4050 dscfm Non-compliance coatings used. Cure cycle set @ 45 minutes. |  |  |  |
| C. COST |  |  |  |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $40,000 INSTALLATION: $5,000 ( ) SOURCE OF COST DATA: |  |  |  |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $3,600 ( ) SOURCE OF COST DATA: |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: Jeanne Pandes Villacorte INSPECTOR'S NAME: DATE: |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: See Source Test Information |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: None DATES: CAUSES: |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |  |  |  |
| D5. FREQUENCY OF MAINTENANCE: Not known |  |  |  |

| 6. COMMENTS |  | App. No.: 335644 |
| --- | --- | --- |