Application No.:  ASPIDC

Equipment Category – Gas Turbine

| 1. GENERAL INFORMATION |  |  | DATE: 5/16/2003 |
| --- | --- | --- | --- |
| a. manufacturer: GE |  |  |  |
| b. type: Combined Cycle |  | c. model: 7FA |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: ASPIDC |
| --- | --- | --- | --- |
| A. FUNCTION: Power Generation (one of two identical gas turbine/HRSG units sharing common steam turbine). No duct burners. Capacity per gas turbine: 170 MW. Capacity of steam turbine: 185 MW. |  |  |  |
| B. maximum Heat Input: 4,064 MMBtu/hr HHV max. (0 deg F), 3,760 MMBtu/hr avg. (50 deg F) |  | C. maximum throughput: |  |
| D. burner information: no.: type: Dry low-NOx burners. |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: |  |
| g. operating conditions: Steady, at or near max. load. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: ASPIDC |  |
| --- | --- | --- | --- | --- |
| A. NAME: IDC Bellingham, LLC |  |  |  | B. SIC CODE: |
| C. ADDRESS: C/o FPL Energy LLC, 700 Universe Blvd., P.O. Box 14000 CITY: Juno Beach STATE: FL ZIP: 33408 |  |  |  |  |
| D. CONTACT PERSON: David C. Shadle |  | E. PHONE NO.: |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: ASPIDC |
| --- | --- | --- | --- | --- |
| A. AGENCY: Massachusetts Dept. of Environmental Protection |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Gary Roscoe |  |  | D. PHONE NO.: 508-792-7650 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: ASPIDC ISSUANCE DATE: 9/11/2000 check if no p/c P/O NO.: ISSUANCE DATE: |  |  |  |  |
| F. START-UP DATE: Project Cancelled |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: ASPIDC |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: ppmvd@15%O2 (1-hr avg.): NOx 1.5 (can be up to 2.0 up for to 10% of operation, based on 12-mo. rolling avg.), CO 2.0, VOC, 1.0, NH3 2.0 (can be up to 5.0 for up to 10% of operation, based on 12-mo. rolling avg.); Lb/MMBtu: PM .008, SO2 .002. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: The limits on NOx, CO, VOC and NH3 are as stringent or more stringent than prior existing SCAQMD BACT for this source category. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: These limits were negotiated with the applicant and are presumably based on vendor guarantees. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: |  |  |  |  |  |
| B2. TYPE: SCR System plus Oxidation Catalyst |  |  |  |  |  |
| B3. DESCRIPTION: |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ASPIDC ISSUANCE DATE: 9/11/2000 P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: CEMS for NOx, CO and NH3. Annual source test for NOx, CO, VOC, PM and NH3. |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: Periodic catalyst replacement/refurbishment. Ammonia storage, handling, injection system maintenance. |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Within 180 days after startup CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: ASPIDC |
| --- | --- | --- |
| The upper limit on NH3, that is allowed for up to 10% of operation, which is initially to be 5.0 ppm, may be reduced to as low as 2.0 ppm depending on the results of a 3-year ammonia emissions monitoring and study program to commence within 180 days following startup. It should be noted that the permit emission limits were never verified by performance data. AQMD learned in May 2003 that the project had been cancelled. |  |  |