Application No.:  S-1135-313-0

Equipment Category – Gas Turbine

| 1. GENERAL INFORMATION |  |  | DATE: 12/18/2001 |
| --- | --- | --- | --- |
| a. manufacturer: General Electric or Westinghouse |  |  |  |
| b. type: Combined-Cycle |  | c. model: GE F7A or Westinghouse 501F |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: S-1135-313-0 |
| --- | --- | --- | --- |
| A. FUNCTION: Power Generation (one of two identical gas turbine/HRSG units sharing common steam turbine). Capacity per gas turbine: 170 MW. Capacity of steam turbine: 160 MW. |  |  |  |
| B. maximum Heat Input: 1,919 MMBtu/hr (gas turbine), 39.5 MMBtu/hr (duct burners) |  | C. maximum throughput: |  |
| D. burner information: no.: type: Dry Low-NOx |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: |  |
| g. operating conditions: Base, Peak, Cycling |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: S-1135-313-0 |  |
| --- | --- | --- | --- | --- |
| A. NAME: Western Midway Sunset Power Project |  |  |  | B. SIC CODE: 4911 |
| C. ADDRESS: 3467 W. Crocker Springs Road CITY: Fellows STATE: CA ZIP: 93224 |  |  |  |  |
| D. CONTACT PERSON: Ed Western |  | E. PHONE NO.: |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: S-1135-313-0 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SJVUAPCD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Melissa Adams |  |  | D. PHONE NO.: 661-326-6900 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: S-1135-313-0 ISSUANCE DATE: 12/12/2000 check if no p/c P/O NO.: ISSUANCE DATE: |  |  |  |  |
| F. START-UP DATE: July 2004 (Est.) |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: S-1135-313-0 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: PPMVD@15%O2: NOx-2(1-hr), CO-4(3-hr)(EPA PSD limit), VOC-1.4 if GE or 1.5 if West. (3-hr), NH3-10(24-hr). Mass limits on NOx, CO, VOC and PM10. Max S in fuel: 0.75 gr/100 dscf. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: The ppm limits on NOx, CO and VOC were believed to represent BACT for combined-cycle gas turbines. The restriction to 0.75 gr/100 dscf max. sulfur in fuel, use of an air inlet filter, combustion controls and use of lube oil vent coalescers were considered BACT for PM10 and SOx. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: The basis for the NOx limit was Mystic Power Plant in Masachusetts, which has been permitted at 2 ppm (1-hr) and Three Mountain Power Project in Shasta County, CA, which has a tentative 2 ppm (1-hr) limit, pending the results of a three year "demonstration" period. The CO and VOC limits were offered by the turbine vendors. Restriction to 0.75 gr/100 dscf max. S in fuel was stated to be "achieved in practice" (supported by the CARB guidance document, in which the Sutter power project is mentioned as being restricted to 0.7 gr/100 dscf). Use of inlet air filters and lube oil vent coalescers was listed as "achieved in Practice" based on "District Guideline #3.4.2". Use of "good combustion controls" does not require anything beyond normal gas turbine combustion controls. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: |  |  |  |  |  |
| B2. TYPE: SCR System and Oxidation Catalyst |  |  |  |  |  |
| B3. DESCRIPTION: |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: S-1135-313-0 ISSUANCE DATE: 12/12/2001 P/O NO.: ISSUANCE DATE: |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: CEMS for NOx and CO. Additional NOx CEMS upstream of SCR (to enable calculation of NH3 slip). Initial and annual source tests |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: Periodic replacement/refurbishment of catalysts; maintenance of NH3 storage and injection system. |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Within 60 days after startup. CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: S-1135-313-0 |
| --- | --- | --- |
| SJVUAPCD initially planned to permit these gas turbines with CO limits of 6 ppmvd (15%O2, 3-hr avg.) based on the CARB Guidance document, but EPA imposed the 4 ppm (1-hr) limit in the PSD permit. It is significant that the permit NOx level accepted by the applicant is the same regardless of whether the gas turbine selected is a GE F7A or a Westinghouse 501F, which generally operates at a higher NOx level. It should be noted that the permit emission limits have not yet been verified by performance data. |  |  |