- Application No.:  118969

- Equipment Category – Gas Turbine

| 1. GENERAL INFORMATION |  |  | DATE: 4/16/2003 |
| --- | --- | --- | --- |
| a. manufacturer: Asea Brown-Boveri (ABB) |  |  |  |
| b. type: Combined Cycle |  | c. model: GT-24 |  |
| d. style: |  |  |  |
| e. applicable aqmd rules: |  |  |  |
| f. cost: $ () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 118969 |
| --- | --- | --- | --- |
| A. FUNCTION: Power generation: two gas turbines rated at 180 MW each (210 MW w/ steam augmentation), two unfired HRSGs, two steam turbines rated at 95 MW each (85 MW in steam augmentation mode) |  |  |  |
| B. maximum Heat Input: 3630 MMBtu/hr, 4367 MMBtu/hr w/ steam augmentation |  | C. maximum throughput: |  |
| D. burner information: no.: type: Dry Low NOx |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: None |  |
| g. operating conditions: Most operation expected to be at or near full capacity w/o steam augmentation. However, due to materials problems, the plant has derated the maximum power output on both power trains to 92% of design capacity. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 118969 |  |
| --- | --- | --- | --- | --- |
| A. NAME: ANP Blackstone Energy Co. |  |  |  | B. SIC CODE: |
| C. ADDRESS: 204 Elm Street CITY: Blackstone STATE: MA ZIP: 01504 |  |  |  |  |
| D. CONTACT PERSON: Robert G. Maggiani |  | E. PHONE NO.: 508-876-8114 |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 118969 |
| --- | --- | --- | --- | --- |
| A. AGENCY: Massachusetts Dept. of Environmental Protection |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Gary Roscoe |  |  | D. PHONE NO.: 508-767-2773 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 118969 ISSUANCE DATE: 4/16/1999 check if no p/c P/O NO.: 118969 ISSUANCE DATE: 3/16/2001 |  |  |  |  |
| F. START-UP DATE: March 2001 |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 118969 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: PPMVD@15%O2 (1-hr block avg.): NOx-2.0, CO-3.0, VOC-1.4 (as CH4), NH3-2.0 except during startups and shutdowns (will be conditioned later on lb-per-event basis). Higher limits (3.5 ppm) are allowed for NOx and VOC in steam-augmentation mode. Higher limits are allowed for CO and VOC at reduced loads: CO-4.0 at 75% load and 20 at 50% load, VOC-2.5 at 50% load. PM limits: 23.9, 19.1 and 14.6 lb/hr at 100%, 75% and 50% load, respectively. Max. sulfur in fuel 0.8 grn/100 cu. ft. Facility-wide TPY limits (12-mo. rolling avg.): NOx-151, CO-437, VOC-49, NH3-47, PM-209, SO2-40, H2SO4-21. |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: PPMVD@15%O2 (1-hr block avg.): NOx-2.0, CO-3.0, VOC-1.4 (as CH4), NH3-2.0 except during startups and shutdowns. Higher limits allowed for NOx and VOC in steam-augmentation mode and for CO and VOC at reduced loads. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: Emission limits were negotiated with the applicant. |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Engelhard (oxidation catalyst), Mitsubishi/Cormetech (SCR) |  |  |  |  |  |
| B2. TYPE: Oxidation catalyst and SCR |  |  |  |  |  |
| B3. DESCRIPTION: |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 118969 ISSUANCE DATE: 4/16/1999 P/O NO.: 118969 ISSUANCE DATE: 3/16/2001 |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |  |  |  |  |  |
| B6. WARRANTY: The plant is guaranteed to meet the permit limits. |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: Oxidation catalyst and SCR have operated well since startup. As of September 30, 2002, both units had over 5,000 hours operation. |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: June 5-7, July 5-12 and Dec 5-6, 2001; Feb 11-12 and May 15 2002 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: PPMVD@15%O2 (VOC as CH4): Unit Date Load NOx CO VOC NH3 1 June 75% 1.6 <0.1 0.2 .06 1 June 50% 1.4 0.5 0.2 .08 2 July 75% 1.5 <0.1 0.4 .02 2 July 50% 1.7 0.8 0.4 0.2 2 Dec 87% 1.4 <0.1 <0.1 .05 1 Feb 87% 1.7 0.3 0.1 0.1 1 May 87% 1.6 0.3 0.1 0.1 2 May 87% 1.6 0.0 0.1 0.1 OPERATING CONDITIONS: Steady TEST METHODS: Test protocol was approved and all tests were formally accepted by Massachusetts DEP. In the July 50%-load test on Unit 2, PM exceeded the limit (19.2 versus 14.6 lb/hr limit). Unit 2 was re-tested at 50% load in December 2001 for PM only, and was well below the limit. |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 118969 |
| --- | --- | --- |
| A NOx monitor on the turbine exhaust indicates that the ABB GT-24 gas turbine operates with NOx mostly in the 11-15 ppmvd range (corrected to 15%O2). Gas turbines with similar low NOx emissions may not be available in smaller sizes needed by some users, and it may be impractical to control NOx to 2.0 ppm on gas turbines with higher NOx levels. These smaller turbines may rely on water or steam injection for NOx control, and control of CO emissions to 3.0 ppmvd may be difficult on these turbines. Results of certified CEMS (as posted on USEPA Acid Rain web site) for the first three quarters in 2002 show NOx in compliance with the 2.0 ppm limit with very few exceptions during over 2300 hours operation of Unit 1 and over 3700 hours operation of Unit 2. More exceedances were observed during the first year of operation (2001--1201 hours on Unit 1 and 1463 hours on Unit 2). This plant has unfired HRSGs. The 3.0 ppmvd (corrected to 15% O2) CO limit at full load may be more difficult to meet on a plant that employs duct burners. |  |  |